## Calculator
TROX AURA SAFE MINI_X-BUS Cable Length Calculator.
Damper data: | Insert data:
Damper operating power (W) | 2.5
Damper hold power (W) | 0.8 |  | Actuator Power:
Wire cross-section (mm2) | 1.5
BFL24-T
Number of smoke detectors | 1 |  | Operating Power | 2.5 | W
|  |  | Hold Power | 0.8 | W
Max number of dampers | Fire control system | Smoke control system
FL-CTRL2 (Lite Controller) | 2 | 7
FL-CTRL1 (Standard Controller) | 26 | 17
FL-BO1 (Booster) | 26 | 8
FL-FEP1-(Fire alarm panel) | 1
Number of dampers | L_max (m) Fire control system | L_max (m) Smoke control system
1 | 866.0526 | 559.0541 | BFN24-T
2 | 548.5 | 333.629 | Operating Power | 4 | W
3 | 401.3415 | 237.7586 | Hold Power | 1.4 | W
4 | 316.4423 | 184.6875
5 | 261.1905 | 150.9854
6 | 222.3649 | 127.6852
7 | 193.5882 | 110.615 | BF24-T
8 | 171.4063 | 97.5708 | Operating Power | 7 | W
9 | 153.785 | 87.2785 | Hold Power | 2 | W
10 | 139.4492 | 78.9504
11 | 127.5581 | 72.0732
12 | 117.5357 | 66.2981
* Cable length is the distance from Controller / Booster to the module located farthest away.

## Actuator info FKA2-EU
Fjærreturaktuator BFL for størrelse 1 | Fjærreturaktuator BFN for størrelse 2 og 3

## Ark1 (hidden)
mm2 | *Unlock sheet: iion
1
1.5
2.5